## Tank Calculator
Inputs | [5 empty] | Calculated / Derived from Sounding Table
Analog_mA | Sensor_Min_bar | Sensor_Max_bar | Density | Dead_Volume | Tank_Height | Level_m | Interp_Volume_m3 | Final_Volume_m3 | Litres | Tonnage | Level_%
4 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0 | 0.03 | 0.06 | 60 | 0.04944 | 0 | data from Wehark
4.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.11598 | 0.31391 | 0.34391 | 343.9114 | 0.28338 | 5.7132 | Sensor output | Height | Volume | Liters | Tonnage(t) | Percentage
5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.23196 | 0.93173 | 0.96173 | 961.7342 | 0.79247 | 11.4264 | (mA) | (m) | (m3) | (L) | (T) | (%)
5.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.34793 | 1.7076 | 1.7376 | 1737.6013 | 1.4318 | 17.1396 | 4 | 0 | 0.14 | 140 | 0.13 | 0
6 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.46391 | 2.4935 | 2.5235 | 2523.4684 | 2.0793 | 22.8528 | 4.5 | 0.101 | 0.322 | 322.38 | 0.31 | 4.67
6.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.57989 | 3.2791 | 3.3091 | 3309.114 | 2.7267 | 28.566 | 5 | 0.201 | 0.615 | 614.76 | 0.58 | 9.35
7 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.69587 | 4.0569 | 4.0869 | 4086.9368 | 3.3676 | 34.2792 | 6 | 0.402 | 1.49 | 1489.53 | 1.42 | 18.7
7.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.81184 | 4.8411 | 4.8711 | 4871.0697 | 4.0138 | 39.9924 | 7 | 0.604 | 2.661 | 2661.44 | 2.53 | 28.05
8 | 0 | 0.3 | 824 | 0.03 | 2.03 | 0.92782 | 5.6226 | 5.6526 | 5652.5825 | 4.6577 | 45.7056 | 8 | 0.805 | 3.938 | 3938.11 | 3.74 | 37.4
8.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.0438 | 6.4028 | 6.4328 | 6432.804 | 5.3006 | 51.4188 | 9 | 1.066 | 5.216 | 5215.73 | 4.95 | 46.75
9 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.1598 | 7.1887 | 7.2187 | 7218.6711 | 5.9482 | 57.1319 | 10 | 1.207 | 6.497 | 6497.17 | 6.17 | 56.09
9.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.2758 | 7.9745 | 8.0045 | 8004.5382 | 6.5957 | 62.8451 | 12 | 1.61 | 9.057 | 9057.17 | 8.6 | 74.79
10 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.3917 | 8.7539 | 8.7839 | 8783.8737 | 7.2379 | 68.5583 | 14 | 2.012 | 11.621 | 11621.46 | 11.04 | 93.49
10.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.5077 | 9.5363 | 9.5663 | 9566.2724 | 7.8826 | 74.2715 | 15 | 2.152 | 12.5 | 12520 | 11.89 | 100
11 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.6237 | 10.3221 | 10.3521 | 10352.1395 | 8.5302 | 79.9847
11.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.7397 | 11.1073 | 11.1373 | 11137.3421 | 9.1772 | 85.6979
12 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.8556 | 11.8852 | 11.9152 | 11915.1649 | 9.8181 | 91.4111
12.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 1.9716 | 12.6697 | 12.6997 | 12699.7408 | 10.4646 | 97.1243 | TANKS | Min_bar | Max_bar | DENSITY | Dead_Volume | Tank_Height
13 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | DIRTY OIL TANK | 0 | 0.2 | 824 | 0.01 | 0.886
13.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FO RU TANK 1 | 0 | 0.2 | 824 | 0.03 | 2.075
14 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FO RU TANK 2 | 0 | 0.2 | 824 | 0.03 | 2.076
14.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FO RU TANK 3 | 0 | 0.2 | 824 | 0.04 | 2.075
15 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FO RU TANK 4 | 0 | 0.2 | 824 | 0.04 | 2.075
15.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FRESH WATER TANK | 0 | 0.3 | 1000 | 0.07 | 2.152
16 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FUEL OIL TANK 1 | 0 | 0.3 | 824 | 0.03 | 2.03
16.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FUEL OIL TANK 2 | 0 | 0.3 | 824 | 0 | 1.98
17 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | FUEL OIL TANK 3 | 0 | 0.2 | 824 | 0.03 | 0.708
17.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | GREY WATER TANK | 0 | 0.3 | 1025 | 0.01 | 2.196
18 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | LO_TANK | 0 | 0.2 | 870 | 0.14 | 0.8
18.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100 | BILGE OIL TANK | 0 | 0.2 | 824 | 0.01 | 0.896
19 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100
19.5 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100
20 | 0 | 0.3 | 824 | 0.03 | 2.03 | 2.03 | 13.06 | 13.09 | 13090 | 10.7862 | 100

## Sounding Table
Level_m | Volume_m3 | Weight
0 | 0.03 | 0.02
0.005 | 0.03 | 0.03
0.01 | 0.04 | 0.03
0.015 | 0.05 | 0.04
0.02 | 0.05 | 0.05
0.025 | 0.06 | 0.05
0.03 | 0.07 | 0.06
0.035 | 0.08 | 0.07
0.04 | 0.09 | 0.08
0.045 | 0.1 | 0.09
0.05 | 0.11 | 0.1
0.055 | 0.12 | 0.11
0.06 | 0.14 | 0.12
0.065 | 0.15 | 0.13
0.07 | 0.16 | 0.14
0.075 | 0.18 | 0.15
0.08 | 0.19 | 0.16
0.085 | 0.21 | 0.18
0.09 | 0.22 | 0.19
0.095 | 0.24 | 0.2
0.1 | 0.26 | 0.22
0.105 | 0.28 | 0.23
0.11 | 0.29 | 0.25
0.115 | 0.31 | 0.27
0.12 | 0.33 | 0.28
0.125 | 0.35 | 0.3
0.13 | 0.37 | 0.32
0.135 | 0.4 | 0.34
0.14 | 0.42 | 0.35
0.145 | 0.44 | 0.37
0.15 | 0.46 | 0.39
0.155 | 0.49 | 0.41
0.16 | 0.51 | 0.43
0.165 | 0.54 | 0.46
0.17 | 0.56 | 0.48
0.175 | 0.59 | 0.5
0.18 | 0.61 | 0.52
0.185 | 0.64 | 0.55
0.19 | 0.67 | 0.57
0.195 | 0.7 | 0.59
0.2 | 0.73 | 0.62
0.205 | 0.76 | 0.64
0.21 | 0.79 | 0.67
0.215 | 0.82 | 0.7
0.22 | 0.85 | 0.72
0.225 | 0.88 | 0.75
0.23 | 0.92 | 0.78
0.235 | 0.95 | 0.81
0.24 | 0.98 | 0.83
0.245 | 1.01 | 0.86
0.25 | 1.05 | 0.89
0.255 | 1.08 | 0.92
0.26 | 1.12 | 0.95
0.265 | 1.15 | 0.98
0.27 | 1.18 | 1.01
0.275 | 1.22 | 1.03
0.28 | 1.25 | 1.06
0.285 | 1.28 | 1.09
0.29 | 1.32 | 1.12
0.295 | 1.35 | 1.15
0.3 | 1.39 | 1.18
0.305 | 1.42 | 1.21
0.31 | 1.45 | 1.24
0.315 | 1.49 | 1.26
0.32 | 1.52 | 1.29
0.325 | 1.55 | 1.32
0.33 | 1.59 | 1.35
0.335 | 1.62 | 1.38
0.34 | 1.66 | 1.41
0.345 | 1.69 | 1.44
0.35 | 1.72 | 1.46
0.355 | 1.76 | 1.49
0.36 | 1.79 | 1.52
0.365 | 1.82 | 1.55
0.37 | 1.86 | 1.58
0.375 | 1.89 | 1.61
0.38 | 1.93 | 1.64
0.385 | 1.96 | 1.67
0.39 | 1.99 | 1.69
0.395 | 2.03 | 1.72
0.4 | 2.06 | 1.75
0.405 | 2.09 | 1.78
0.41 | 2.13 | 1.81
0.415 | 2.16 | 1.84
0.42 | 2.2 | 1.87
0.425 | 2.23 | 1.89
0.43 | 2.26 | 1.92
0.435 | 2.3 | 1.95
0.44 | 2.33 | 1.98
0.445 | 2.36 | 2.01
0.45 | 2.4 | 2.04
0.455 | 2.43 | 2.07
0.46 | 2.47 | 2.1
0.465 | 2.5 | 2.12
0.47 | 2.53 | 2.15
0.475 | 2.57 | 2.18
0.48 | 2.6 | 2.21
0.485 | 2.63 | 2.24
0.49 | 2.67 | 2.27
0.495 | 2.7 | 2.3
0.5 | 2.74 | 2.33
0.505 | 2.77 | 2.35
0.51 | 2.8 | 2.38
0.515 | 2.84 | 2.41
0.52 | 2.87 | 2.44
0.525 | 2.9 | 2.47
0.53 | 2.94 | 2.5
0.535 | 2.97 | 2.53
0.54 | 3.01 | 2.55
0.545 | 3.04 | 2.58
0.55 | 3.07 | 2.61
0.555 | 3.11 | 2.64
0.56 | 3.14 | 2.67
0.565 | 3.17 | 2.7
0.57 | 3.21 | 2.73
0.575 | 3.24 | 2.76
0.58 | 3.28 | 2.78
0.585 | 3.31 | 2.81
0.59 | 3.34 | 2.84
0.595 | 3.38 | 2.87
0.6 | 3.41 | 2.9
0.605 | 3.44 | 2.93
0.61 | 3.48 | 2.96
0.615 | 3.51 | 2.99
0.62 | 3.55 | 3.01
0.625 | 3.58 | 3.04
0.63 | 3.61 | 3.07
0.635 | 3.65 | 3.1
0.64 | 3.68 | 3.13
0.645 | 3.71 | 3.16
0.65 | 3.75 | 3.19
0.655 | 3.78 | 3.21
0.66 | 3.82 | 3.24
0.665 | 3.85 | 3.27
0.67 | 3.88 | 3.3
0.675 | 3.92 | 3.33
0.68 | 3.95 | 3.36
0.685 | 3.98 | 3.39
0.69 | 4.02 | 3.42
0.695 | 4.05 | 3.44
0.7 | 4.09 | 3.47
0.705 | 4.12 | 3.5
0.71 | 4.15 | 3.53
0.715 | 4.19 | 3.56
0.72 | 4.22 | 3.59
0.725 | 4.25 | 3.62
0.73 | 4.29 | 3.64
0.735 | 4.32 | 3.67
0.74 | 4.36 | 3.7
0.745 | 4.39 | 3.73
0.75 | 4.42 | 3.76
0.755 | 4.46 | 3.79
0.76 | 4.49 | 3.82
0.765 | 4.52 | 3.85
0.77 | 4.56 | 3.87
0.775 | 4.59 | 3.9
0.78 | 4.63 | 3.93
0.785 | 4.66 | 3.96
0.79 | 4.69 | 3.99
0.795 | 4.73 | 4.02
0.8 | 4.76 | 4.05
0.805 | 4.79 | 4.08
0.81 | 4.83 | 4.1
0.815 | 4.86 | 4.13
0.82 | 4.9 | 4.16
0.825 | 4.93 | 4.19
0.83 | 4.96 | 4.22
0.835 | 5 | 4.25
0.84 | 5.03 | 4.28
0.845 | 5.06 | 4.3
0.85 | 5.1 | 4.33
0.855 | 5.13 | 4.36
0.86 | 5.17 | 4.39
0.865 | 5.2 | 4.42
0.87 | 5.23 | 4.45
0.875 | 5.27 | 4.48
0.88 | 5.3 | 4.51
0.885 | 5.33 | 4.53
0.89 | 5.37 | 4.56
0.895 | 5.4 | 4.59
0.9 | 5.44 | 4.62
0.905 | 5.47 | 4.65
0.91 | 5.5 | 4.68
0.915 | 5.54 | 4.71
0.92 | 5.57 | 4.74
0.925 | 5.6 | 4.76
0.93 | 5.64 | 4.79
0.935 | 5.67 | 4.82
0.94 | 5.71 | 4.85
0.945 | 5.74 | 4.88
0.95 | 5.77 | 4.91
0.955 | 5.81 | 4.94
0.96 | 5.84 | 4.96
0.965 | 5.87 | 4.99
0.97 | 5.91 | 5.02
0.975 | 5.94 | 5.05
0.98 | 5.98 | 5.08
0.985 | 6.01 | 5.11
0.99 | 6.04 | 5.14
0.995 | 6.08 | 5.17
1 | 6.11 | 5.19
1.005 | 6.14 | 5.22
1.01 | 6.18 | 5.25
1.015 | 6.21 | 5.28
1.02 | 6.25 | 5.31
1.025 | 6.28 | 5.34
1.03 | 6.31 | 5.37
1.035 | 6.35 | 5.39
1.04 | 6.38 | 5.42
1.045 | 6.41 | 5.45
1.05 | 6.45 | 5.48
1.055 | 6.48 | 5.51
1.06 | 6.52 | 5.54
1.065 | 6.55 | 5.57
1.07 | 6.58 | 5.6
1.075 | 6.62 | 5.62
1.08 | 6.65 | 5.65
1.085 | 6.68 | 5.68
1.09 | 6.72 | 5.71
1.095 | 6.75 | 5.74
1.1 | 6.79 | 5.77
1.105 | 6.82 | 5.8
1.11 | 6.85 | 5.83
1.115 | 6.89 | 5.85
1.12 | 6.92 | 5.88
1.125 | 6.95 | 5.91
1.13 | 6.99 | 5.94
1.135 | 7.02 | 5.97
1.14 | 7.06 | 6
1.145 | 7.09 | 6.03
1.15 | 7.12 | 6.05
1.155 | 7.16 | 6.08
1.16 | 7.19 | 6.11
1.165 | 7.22 | 6.14
1.17 | 7.26 | 6.17
1.175 | 7.29 | 6.2
1.18 | 7.33 | 6.23
1.185 | 7.36 | 6.26
1.19 | 7.39 | 6.28
1.195 | 7.43 | 6.31
1.2 | 7.46 | 6.34
1.205 | 7.49 | 6.37
1.21 | 7.53 | 6.4
1.215 | 7.56 | 6.43
1.22 | 7.6 | 6.46
1.225 | 7.63 | 6.48
1.23 | 7.66 | 6.51
1.235 | 7.7 | 6.54
1.24 | 7.73 | 6.57
1.245 | 7.76 | 6.6
1.25 | 7.8 | 6.63
1.255 | 7.83 | 6.66
1.26 | 7.87 | 6.69
1.265 | 7.9 | 6.71
1.27 | 7.93 | 6.74
1.275 | 7.97 | 6.77
1.28 | 8 | 6.8
1.285 | 8.03 | 6.83
1.29 | 8.07 | 6.86
1.295 | 8.1 | 6.89
1.3 | 8.14 | 6.92
1.305 | 8.17 | 6.94
1.31 | 8.2 | 6.97
1.315 | 8.24 | 7
1.32 | 8.27 | 7.03
1.325 | 8.3 | 7.06
1.33 | 8.34 | 7.09
1.335 | 8.37 | 7.12
1.34 | 8.41 | 7.14
1.345 | 8.44 | 7.17
1.35 | 8.47 | 7.2
1.355 | 8.51 | 7.23
1.36 | 8.54 | 7.26
1.365 | 8.57 | 7.29
1.37 | 8.61 | 7.32
1.375 | 8.64 | 7.35
1.38 | 8.68 | 7.37
1.385 | 8.71 | 7.4
1.39 | 8.74 | 7.43
1.395 | 8.78 | 7.46
1.4 | 8.81 | 7.49
1.405 | 8.84 | 7.52
1.41 | 8.88 | 7.55
1.415 | 8.91 | 7.58
1.42 | 8.95 | 7.6
1.425 | 8.98 | 7.63
1.43 | 9.01 | 7.66
1.435 | 9.05 | 7.69
1.44 | 9.08 | 7.72
1.445 | 9.11 | 7.75
1.45 | 9.15 | 7.78
1.455 | 9.18 | 7.8
1.46 | 9.22 | 7.83
1.465 | 9.25 | 7.86
1.47 | 9.28 | 7.89
1.475 | 9.32 | 7.92
1.48 | 9.35 | 7.95
1.485 | 9.38 | 7.98
1.49 | 9.42 | 8.01
1.495 | 9.45 | 8.03
1.5 | 9.49 | 8.06
1.505 | 9.52 | 8.09
1.51 | 9.55 | 8.12
1.515 | 9.59 | 8.15
1.52 | 9.62 | 8.18
1.525 | 9.65 | 8.21
1.53 | 9.69 | 8.23
1.535 | 9.72 | 8.26
1.54 | 9.76 | 8.29
1.545 | 9.79 | 8.32
1.55 | 9.82 | 8.35
1.555 | 9.86 | 8.38
1.56 | 9.89 | 8.41
1.565 | 9.92 | 8.44
1.57 | 9.96 | 8.46
1.575 | 9.99 | 8.49
1.58 | 10.03 | 8.52
1.585 | 10.06 | 8.55
1.59 | 10.09 | 8.58
1.595 | 10.13 | 8.61
1.6 | 10.16 | 8.64
1.605 | 10.19 | 8.67
1.61 | 10.23 | 8.69
1.615 | 10.26 | 8.72
1.62 | 10.3 | 8.75
1.625 | 10.33 | 8.78
1.63 | 10.36 | 8.81
1.635 | 10.4 | 8.84
1.64 | 10.43 | 8.87
1.645 | 10.46 | 8.89
1.65 | 10.5 | 8.92
1.655 | 10.53 | 8.95
1.66 | 10.57 | 8.98
1.665 | 10.6 | 9.01
1.67 | 10.63 | 9.04
1.675 | 10.67 | 9.07
1.68 | 10.7 | 9.1
1.685 | 10.73 | 9.12
1.69 | 10.77 | 9.15
1.695 | 10.8 | 9.18
1.7 | 10.84 | 9.21
1.705 | 10.87 | 9.24
1.71 | 10.9 | 9.27
1.715 | 10.94 | 9.3
1.72 | 10.97 | 9.33
1.725 | 11 | 9.35
1.73 | 11.04 | 9.38
1.735 | 11.07 | 9.41
1.74 | 11.11 | 9.44
1.745 | 11.14 | 9.47
1.75 | 11.17 | 9.5
1.755 | 11.21 | 9.53
1.76 | 11.24 | 9.55
1.765 | 11.27 | 9.58
1.77 | 11.31 | 9.61
1.775 | 11.34 | 9.64
1.78 | 11.38 | 9.67
1.785 | 11.41 | 9.7
1.79 | 11.44 | 9.73
1.795 | 11.48 | 9.76
1.8 | 11.51 | 9.78
1.805 | 11.54 | 9.81
1.81 | 11.58 | 9.84
1.815 | 11.61 | 9.87
1.82 | 11.65 | 9.9
1.825 | 11.68 | 9.93
1.83 | 11.71 | 9.96
1.835 | 11.75 | 9.98
1.84 | 11.78 | 10.01
1.845 | 11.81 | 10.04
1.85 | 11.85 | 10.07
1.855 | 11.88 | 10.1
1.86 | 11.92 | 10.13
1.865 | 11.95 | 10.16
1.87 | 11.98 | 10.19
1.875 | 12.02 | 10.21
1.88 | 12.05 | 10.24
1.885 | 12.08 | 10.27
1.89 | 12.12 | 10.3
1.895 | 12.15 | 10.33
1.9 | 12.19 | 10.36
1.905 | 12.22 | 10.39
1.91 | 12.25 | 10.42
1.915 | 12.29 | 10.44
1.92 | 12.32 | 10.47
1.925 | 12.35 | 10.5
1.93 | 12.39 | 10.53
1.935 | 12.42 | 10.56
1.94 | 12.46 | 10.59
1.945 | 12.49 | 10.62
1.95 | 12.52 | 10.64
1.955 | 12.56 | 10.67
1.96 | 12.59 | 10.7
1.965 | 12.62 | 10.73
1.97 | 12.66 | 10.76
1.975 | 12.69 | 10.79
1.98 | 12.73 | 10.82
1.985 | 12.76 | 10.85
1.99 | 12.79 | 10.87
1.995 | 12.83 | 10.9
2 | 12.86 | 10.93
2.005 | 12.89 | 10.96
2.01 | 12.93 | 10.99
2.015 | 12.96 | 11.02
2.02 | 13 | 11.05
2.025 | 13.03 | 11.07
2.03 | 13.06 | 11.1
2.03 | 13.06 | 11.1

## Sounding Table (2) (hidden)
Level_m | Volume_m3 | Weight | Correction_factor | Revised Value | Level_m | Volume_m3 | Correction_factor | Level_m | Volume_m3 | Level_m | Volume_m3 | Volume_m3 | Correction_factor
0 | 0.03 | 0.02 | 0 | 0.03 | 0 | 0.03 | 0.01 | 0 | 0.03 | 0 | 0.03 | 0.04 | 0.01
0.005 | 0.03 | 0.03 | 0.01 | 0.04 | 0.1 | 0.23 | -0.03 | 0.005 | 0.04 | 0.1 | 0.26 | 0.23 | -0.03
0.01 | 0.04 | 0.03 | 0.01 | 0.05 | 0.2 | 0.85 | 0.12 | 0.01 | 0.05 | 0.2 | 0.73 | 0.85 | 0.12
0.015 | 0.05 | 0.04 | 0.01 | 0.06 | 0.3 | 1.15 | -0.24 | 0.015 | 0.06 | 0.3 | 1.39 | 1.15 | -0.24
0.02 | 0.05 | 0.05 | 0.02 | 0.07 | 0.4 | 2 | -0.06 | 0.02 | 0.07 | 0.4 | 2.06 | 2 | -0.06
0.025 | 0.06 | 0.05 | 0.02 | 0.08 | 0.5 | 2.5 | -0.24 | 0.025 | 0.08 | 0.5 | 2.74 | 2.5 | -0.24
0.03 | 0.07 | 0.06 | 0.02 | 0.09 | 0.6 | 3.23 | -0.18 | 0.03 | 0.09 | 0.6 | 3.41 | 3.23 | -0.18
0.035 | 0.08 | 0.07 | 0.02 | 0.1 | 0.7 | 4.25 | 0.16 | 0.035 | 0.1 | 0.7 | 4.09 | 4.25 | 0.16
0.04 | 0.09 | 0.08 | 0.02 | 0.11 | 0.8 | 4.9 | 0.14 | 0.04 | 0.11 | 0.8 | 4.76 | 4.9 | 0.14
0.045 | 0.1 | 0.09 | 0.02 | 0.12 | 0.9 | 5.25 | -0.19 | 0.045 | 0.12 | 0.9 | 5.44 | 5.25 | -0.19
0.05 | 0.11 | 0.1 | 0.02 | 0.13 | 1 | 6 | -0.11 | 0.05 | 0.13 | 1 | 6.11 | 6 | -0.11
0.055 | 0.12 | 0.11 | 0.02 | 0.14 | 1.1 | 6.5 | -0.29 | 0.055 | 0.14 | 1.1 | 6.79 | 6.5 | -0.29
0.06 | 0.14 | 0.12 | 0.01 | 0.15 | 1.2 | 7.35 | -0.11 | 0.06 | 0.15 | 1.2 | 7.46 | 7.35 | -0.11
0.065 | 0.15 | 0.13 | 0.01 | 0.16 | 1.3 | 8 | -0.14 | 0.065 | 0.16 | 1.3 | 8.14 | 8 | -0.14
0.07 | 0.16 | 0.14 | 0.01 | 0.17 | 1.4 | 9 | 0.19 | 0.07 | 0.17 | 1.4 | 8.81 | 9 | 0.19
0.075 | 0.18 | 0.15 | 0 | 0.18 | 1.5 | 9.5 | 0.01 | 0.075 | 0.18 | 1.5 | 9.49 | 9.5 | 0.01
0.08 | 0.19 | 0.16 | 0 | 0.19 | 1.6 | 10 | -0.16 | 0.08 | 0.19 | 1.6 | 10.16 | 10 | -0.16
0.085 | 0.21 | 0.18 | -0.01 | 0.2 | 1.7 | 10.95 | 0.11 | 0.085 | 0.2 | 1.7 | 10.84 | 10.95 | 0.11
0.09 | 0.22 | 0.19 | -0.01 | 0.21 | 1.8 | 11.8 | 0.29 | 0.09 | 0.21 | 1.8 | 11.51 | 11.8 | 0.29
0.095 | 0.24 | 0.2 | -0.02 | 0.22 | 1.9 | 12 | -0.19 | 0.095 | 0.22 | 1.9 | 12.19 | 12 | -0.19
0.1 | 0.26 | 0.22 | -0.03 | 0.23 | 2 | 12.5 | -0.36 | 0.1 | 0.23 | 2 | 12.86 | 12.5 | -0.36
0.105 | 0.28 | 0.23 |  |  | 2.03 | 13 | -0.06 | 0.105 | 0.28 | 2.03 | 13.06 | 13 | -0.06
0.11 | 0.29 | 0.25 | [5 empty] | 0.11 | 0.29
0.115 | 0.31 | 0.27 | [5 empty] | 0.115 | 0.31
0.12 | 0.33 | 0.28 | [5 empty] | 0.12 | 0.33
0.125 | 0.35 | 0.3 | [5 empty] | 0.125 | 0.35
0.13 | 0.37 | 0.32 | [5 empty] | 0.13 | 0.37
0.135 | 0.4 | 0.34 | [5 empty] | 0.135 | 0.4
0.14 | 0.42 | 0.35 | [5 empty] | 0.14 | 0.42
0.145 | 0.44 | 0.37 | [5 empty] | 0.145 | 0.44
0.15 | 0.46 | 0.39 | [5 empty] | 0.15 | 0.46
0.155 | 0.49 | 0.41 | [5 empty] | 0.155 | 0.49
0.16 | 0.51 | 0.43 | [5 empty] | 0.16 | 0.51
0.165 | 0.54 | 0.46 | [5 empty] | 0.165 | 0.54
0.17 | 0.56 | 0.48 | [5 empty] | 0.17 | 0.56
0.175 | 0.59 | 0.5 | [5 empty] | 0.175 | 0.59
0.18 | 0.61 | 0.52 | [5 empty] | 0.18 | 0.61
0.185 | 0.64 | 0.55 | [5 empty] | 0.185 | 0.64
0.19 | 0.67 | 0.57 | [5 empty] | 0.19 | 0.67
0.195 | 0.7 | 0.59 | [5 empty] | 0.195 | 0.7
0.2 | 0.73 | 0.62 | 0.12 |  |  |  |  | 0.2 | 0.73
0.205 | 0.76 | 0.64 | [5 empty] | 0.205 | 0.76
0.21 | 0.79 | 0.67 | [5 empty] | 0.21 | 0.79
0.215 | 0.82 | 0.7 | [5 empty] | 0.215 | 0.82
0.22 | 0.85 | 0.72 | [5 empty] | 0.22 | 0.85
0.225 | 0.88 | 0.75 | [5 empty] | 0.225 | 0.88
0.23 | 0.92 | 0.78 | [5 empty] | 0.23 | 0.92
0.235 | 0.95 | 0.81 | [5 empty] | 0.235 | 0.95
0.24 | 0.98 | 0.83 | [5 empty] | 0.24 | 0.98
0.245 | 1.01 | 0.86 | [5 empty] | 0.245 | 1.01
0.25 | 1.05 | 0.89 | [5 empty] | 0.25 | 1.05
0.255 | 1.08 | 0.92 | [5 empty] | 0.255 | 1.08
0.26 | 1.12 | 0.95 | [5 empty] | 0.26 | 1.12
0.265 | 1.15 | 0.98 | [5 empty] | 0.265 | 1.15
0.27 | 1.18 | 1.01 | [5 empty] | 0.27 | 1.18
0.275 | 1.22 | 1.03 | [5 empty] | 0.275 | 1.22
0.28 | 1.25 | 1.06 | [5 empty] | 0.28 | 1.25
0.285 | 1.28 | 1.09 | [5 empty] | 0.285 | 1.28
0.29 | 1.32 | 1.12 | [5 empty] | 0.29 | 1.32
0.295 | 1.35 | 1.15 | [5 empty] | 0.295 | 1.35
0.3 | 1.39 | 1.18 | -0.24 |  |  |  |  | 0.3 | 1.39
0.305 | 1.42 | 1.21 | [5 empty] | 0.305 | 1.42
0.31 | 1.45 | 1.24 | [5 empty] | 0.31 | 1.45
0.315 | 1.49 | 1.26 | [5 empty] | 0.315 | 1.49
0.32 | 1.52 | 1.29 | [5 empty] | 0.32 | 1.52
0.325 | 1.55 | 1.32 | [5 empty] | 0.325 | 1.55
0.33 | 1.59 | 1.35 | [5 empty] | 0.33 | 1.59
0.335 | 1.62 | 1.38 | [5 empty] | 0.335 | 1.62
0.34 | 1.66 | 1.41 | [5 empty] | 0.34 | 1.66
0.345 | 1.69 | 1.44 | [5 empty] | 0.345 | 1.69
0.35 | 1.72 | 1.46 | [5 empty] | 0.35 | 1.72
0.355 | 1.76 | 1.49 | [5 empty] | 0.355 | 1.76
0.36 | 1.79 | 1.52 | [5 empty] | 0.36 | 1.79
0.365 | 1.82 | 1.55 | [5 empty] | 0.365 | 1.82
0.37 | 1.86 | 1.58 | [5 empty] | 0.37 | 1.86
0.375 | 1.89 | 1.61 | [5 empty] | 0.375 | 1.89
0.38 | 1.93 | 1.64 | [5 empty] | 0.38 | 1.93
0.385 | 1.96 | 1.67 | [5 empty] | 0.385 | 1.96
0.39 | 1.99 | 1.69 | [5 empty] | 0.39 | 1.99
0.395 | 2.03 | 1.72 | [5 empty] | 0.395 | 2.03
0.4 | 2.06 | 1.75 | -0.06 |  |  |  |  | 0.4 | 2.06
0.405 | 2.09 | 1.78 | [5 empty] | 0.405 | 2.09
0.41 | 2.13 | 1.81 | [5 empty] | 0.41 | 2.13
0.415 | 2.16 | 1.84 | [5 empty] | 0.415 | 2.16
0.42 | 2.2 | 1.87 | [5 empty] | 0.42 | 2.2
0.425 | 2.23 | 1.89 | [5 empty] | 0.425 | 2.23
0.43 | 2.26 | 1.92 | [5 empty] | 0.43 | 2.26
0.435 | 2.3 | 1.95 | [5 empty] | 0.435 | 2.3
0.44 | 2.33 | 1.98 | [5 empty] | 0.44 | 2.33
0.445 | 2.36 | 2.01 | [5 empty] | 0.445 | 2.36
0.45 | 2.4 | 2.04 | [5 empty] | 0.45 | 2.4
0.455 | 2.43 | 2.07 | [5 empty] | 0.455 | 2.43
0.46 | 2.47 | 2.1 | [5 empty] | 0.46 | 2.47
0.465 | 2.5 | 2.12 | [5 empty] | 0.465 | 2.5
0.47 | 2.53 | 2.15 | [5 empty] | 0.47 | 2.53
0.475 | 2.57 | 2.18 | [5 empty] | 0.475 | 2.57
0.48 | 2.6 | 2.21 | [5 empty] | 0.48 | 2.6
0.485 | 2.63 | 2.24 | [5 empty] | 0.485 | 2.63
0.49 | 2.67 | 2.27 | [5 empty] | 0.49 | 2.67
0.495 | 2.7 | 2.3 | [5 empty] | 0.495 | 2.7
0.5 | 2.74 | 2.33 | -0.24 |  |  |  |  | 0.5 | 2.74
0.505 | 2.77 | 2.35 | [5 empty] | 0.505 | 2.77
0.51 | 2.8 | 2.38 | [5 empty] | 0.51 | 2.8
0.515 | 2.84 | 2.41 | [5 empty] | 0.515 | 2.84
0.52 | 2.87 | 2.44 | [5 empty] | 0.52 | 2.87
0.525 | 2.9 | 2.47 | [5 empty] | 0.525 | 2.9
0.53 | 2.94 | 2.5 | [5 empty] | 0.53 | 2.94
0.535 | 2.97 | 2.53 | [5 empty] | 0.535 | 2.97
0.54 | 3.01 | 2.55 | [5 empty] | 0.54 | 3.01
0.545 | 3.04 | 2.58 | [5 empty] | 0.545 | 3.04
0.55 | 3.07 | 2.61 | [5 empty] | 0.55 | 3.07
0.555 | 3.11 | 2.64 | [5 empty] | 0.555 | 3.11
0.56 | 3.14 | 2.67 | [5 empty] | 0.56 | 3.14
0.565 | 3.17 | 2.7 | [5 empty] | 0.565 | 3.17
0.57 | 3.21 | 2.73 | [5 empty] | 0.57 | 3.21
0.575 | 3.24 | 2.76 | [5 empty] | 0.575 | 3.24
0.58 | 3.28 | 2.78 | [5 empty] | 0.58 | 3.28
0.585 | 3.31 | 2.81 | [5 empty] | 0.585 | 3.31
0.59 | 3.34 | 2.84 | [5 empty] | 0.59 | 3.34
0.595 | 3.38 | 2.87 | [5 empty] | 0.595 | 3.38
0.6 | 3.41 | 2.9 | -0.18 |  |  |  |  | 0.6 | 3.41
0.605 | 3.44 | 2.93 | [5 empty] | 0.605 | 3.44
0.61 | 3.48 | 2.96 | [5 empty] | 0.61 | 3.48
0.615 | 3.51 | 2.99 | [5 empty] | 0.615 | 3.51
0.62 | 3.55 | 3.01 | [5 empty] | 0.62 | 3.55
0.625 | 3.58 | 3.04 | [5 empty] | 0.625 | 3.58
0.63 | 3.61 | 3.07 | [5 empty] | 0.63 | 3.61
0.635 | 3.65 | 3.1 | [5 empty] | 0.635 | 3.65
0.64 | 3.68 | 3.13 | [5 empty] | 0.64 | 3.68
0.645 | 3.71 | 3.16 | [5 empty] | 0.645 | 3.71
0.65 | 3.75 | 3.19 | [5 empty] | 0.65 | 3.75
0.655 | 3.78 | 3.21 | [5 empty] | 0.655 | 3.78
0.66 | 3.82 | 3.24 | [5 empty] | 0.66 | 3.82
0.665 | 3.85 | 3.27 | [5 empty] | 0.665 | 3.85
0.67 | 3.88 | 3.3 | [5 empty] | 0.67 | 3.88
0.675 | 3.92 | 3.33 | [5 empty] | 0.675 | 3.92
0.68 | 3.95 | 3.36 | [5 empty] | 0.68 | 3.95
0.685 | 3.98 | 3.39 | [5 empty] | 0.685 | 3.98
0.69 | 4.02 | 3.42 | [5 empty] | 0.69 | 4.02
0.695 | 4.05 | 3.44 | [5 empty] | 0.695 | 4.05
0.7 | 4.09 | 3.47 | 0.16 |  |  |  |  | 0.7 | 4.09
0.705 | 4.12 | 3.5 | [5 empty] | 0.705 | 4.12
0.71 | 4.15 | 3.53 | [5 empty] | 0.71 | 4.15
0.715 | 4.19 | 3.56 | [5 empty] | 0.715 | 4.19
0.72 | 4.22 | 3.59 | [5 empty] | 0.72 | 4.22
0.725 | 4.25 | 3.62 | [5 empty] | 0.725 | 4.25
0.73 | 4.29 | 3.64 | [5 empty] | 0.73 | 4.29
0.735 | 4.32 | 3.67 | [5 empty] | 0.735 | 4.32
0.74 | 4.36 | 3.7 | [5 empty] | 0.74 | 4.36
0.745 | 4.39 | 3.73 | [5 empty] | 0.745 | 4.39
0.75 | 4.42 | 3.76 | [5 empty] | 0.75 | 4.42
0.755 | 4.46 | 3.79 | [5 empty] | 0.755 | 4.46
0.76 | 4.49 | 3.82 | [5 empty] | 0.76 | 4.49
0.765 | 4.52 | 3.85 | [5 empty] | 0.765 | 4.52
0.77 | 4.56 | 3.87 | [5 empty] | 0.77 | 4.56
0.775 | 4.59 | 3.9 | [5 empty] | 0.775 | 4.59
0.78 | 4.63 | 3.93 | [5 empty] | 0.78 | 4.63
0.785 | 4.66 | 3.96 | [5 empty] | 0.785 | 4.66
0.79 | 4.69 | 3.99 | [5 empty] | 0.79 | 4.69
0.795 | 4.73 | 4.02 | [5 empty] | 0.795 | 4.73
0.8 | 4.76 | 4.05 | 0.14 |  |  |  |  | 0.8 | 4.76
0.805 | 4.79 | 4.08 | [5 empty] | 0.805 | 4.79
0.81 | 4.83 | 4.1 | [5 empty] | 0.81 | 4.83
0.815 | 4.86 | 4.13 | [5 empty] | 0.815 | 4.86
0.82 | 4.9 | 4.16 | [5 empty] | 0.82 | 4.9
0.825 | 4.93 | 4.19 | [5 empty] | 0.825 | 4.93
0.83 | 4.96 | 4.22 | [5 empty] | 0.83 | 4.96
0.835 | 5 | 4.25 | [5 empty] | 0.835 | 5
0.84 | 5.03 | 4.28 | [5 empty] | 0.84 | 5.03
0.845 | 5.06 | 4.3 | [5 empty] | 0.845 | 5.06
0.85 | 5.1 | 4.33 | [5 empty] | 0.85 | 5.1
0.855 | 5.13 | 4.36 | [5 empty] | 0.855 | 5.13
0.86 | 5.17 | 4.39 | [5 empty] | 0.86 | 5.17
0.865 | 5.2 | 4.42 | [5 empty] | 0.865 | 5.2
0.87 | 5.23 | 4.45 | [5 empty] | 0.87 | 5.23
0.875 | 5.27 | 4.48 | [5 empty] | 0.875 | 5.27
0.88 | 5.3 | 4.51 | [5 empty] | 0.88 | 5.3
0.885 | 5.33 | 4.53 | [5 empty] | 0.885 | 5.33
0.89 | 5.37 | 4.56 | [5 empty] | 0.89 | 5.37
0.895 | 5.4 | 4.59 | [5 empty] | 0.895 | 5.4
0.9 | 5.44 | 4.62 | -0.19 |  |  |  |  | 0.9 | 5.44
0.905 | 5.47 | 4.65 | [5 empty] | 0.905 | 5.47
0.91 | 5.5 | 4.68 | [5 empty] | 0.91 | 5.5
0.915 | 5.54 | 4.71 | [5 empty] | 0.915 | 5.54
0.92 | 5.57 | 4.74 | [5 empty] | 0.92 | 5.57
0.925 | 5.6 | 4.76 | [5 empty] | 0.925 | 5.6
0.93 | 5.64 | 4.79 | [5 empty] | 0.93 | 5.64
0.935 | 5.67 | 4.82 | [5 empty] | 0.935 | 5.67
0.94 | 5.71 | 4.85 | [5 empty] | 0.94 | 5.71
0.945 | 5.74 | 4.88 | [5 empty] | 0.945 | 5.74
0.95 | 5.77 | 4.91 | [5 empty] | 0.95 | 5.77
0.955 | 5.81 | 4.94 | [5 empty] | 0.955 | 5.81
0.96 | 5.84 | 4.96 | [5 empty] | 0.96 | 5.84
0.965 | 5.87 | 4.99 | [5 empty] | 0.965 | 5.87
0.97 | 5.91 | 5.02 | [5 empty] | 0.97 | 5.91
0.975 | 5.94 | 5.05 | [5 empty] | 0.975 | 5.94
0.98 | 5.98 | 5.08 | [5 empty] | 0.98 | 5.98
0.985 | 6.01 | 5.11 | [5 empty] | 0.985 | 6.01
0.99 | 6.04 | 5.14 | [5 empty] | 0.99 | 6.04
0.995 | 6.08 | 5.17 | [5 empty] | 0.995 | 6.08
1 | 6.11 | 5.19 | -0.11 |  |  |  |  | 1 | 6.11
1.005 | 6.14 | 5.22 | [5 empty] | 1.005 | 6.14
1.01 | 6.18 | 5.25 | [5 empty] | 1.01 | 6.18
1.015 | 6.21 | 5.28 | [5 empty] | 1.015 | 6.21
1.02 | 6.25 | 5.31 | [5 empty] | 1.02 | 6.25
1.025 | 6.28 | 5.34 | [5 empty] | 1.025 | 6.28
1.03 | 6.31 | 5.37 | [5 empty] | 1.03 | 6.31
1.035 | 6.35 | 5.39 | [5 empty] | 1.035 | 6.35
1.04 | 6.38 | 5.42 | [5 empty] | 1.04 | 6.38
1.045 | 6.41 | 5.45 | [5 empty] | 1.045 | 6.41
1.05 | 6.45 | 5.48 | [5 empty] | 1.05 | 6.45
1.055 | 6.48 | 5.51 | [5 empty] | 1.055 | 6.48
1.06 | 6.52 | 5.54 | [5 empty] | 1.06 | 6.52
1.065 | 6.55 | 5.57 | [5 empty] | 1.065 | 6.55
1.07 | 6.58 | 5.6 | [5 empty] | 1.07 | 6.58
1.075 | 6.62 | 5.62 | [5 empty] | 1.075 | 6.62
1.08 | 6.65 | 5.65 | [5 empty] | 1.08 | 6.65
1.085 | 6.68 | 5.68 | [5 empty] | 1.085 | 6.68
1.09 | 6.72 | 5.71 | [5 empty] | 1.09 | 6.72
1.095 | 6.75 | 5.74 | [5 empty] | 1.095 | 6.75
1.1 | 6.79 | 5.77 | -0.29 |  |  |  |  | 1.1 | 6.79
1.105 | 6.82 | 5.8 | [5 empty] | 1.105 | 6.82
1.11 | 6.85 | 5.83 | [5 empty] | 1.11 | 6.85
1.115 | 6.89 | 5.85 | [5 empty] | 1.115 | 6.89
1.12 | 6.92 | 5.88 | [5 empty] | 1.12 | 6.92
1.125 | 6.95 | 5.91 | [5 empty] | 1.125 | 6.95
1.13 | 6.99 | 5.94 | [5 empty] | 1.13 | 6.99
1.135 | 7.02 | 5.97 | [5 empty] | 1.135 | 7.02
1.14 | 7.06 | 6 | [5 empty] | 1.14 | 7.06
1.145 | 7.09 | 6.03 | [5 empty] | 1.145 | 7.09
1.15 | 7.12 | 6.05 | [5 empty] | 1.15 | 7.12
1.155 | 7.16 | 6.08 | [5 empty] | 1.155 | 7.16
1.16 | 7.19 | 6.11 | [5 empty] | 1.16 | 7.19
1.165 | 7.22 | 6.14 | [5 empty] | 1.165 | 7.22
1.17 | 7.26 | 6.17 | [5 empty] | 1.17 | 7.26
1.175 | 7.29 | 6.2 | [5 empty] | 1.175 | 7.29
1.18 | 7.33 | 6.23 | [5 empty] | 1.18 | 7.33
1.185 | 7.36 | 6.26 | [5 empty] | 1.185 | 7.36
1.19 | 7.39 | 6.28 | [5 empty] | 1.19 | 7.39
1.195 | 7.43 | 6.31 | [5 empty] | 1.195 | 7.43
1.2 | 7.46 | 6.34 | -0.11 |  |  |  |  | 1.2 | 7.46
1.205 | 7.49 | 6.37 | [5 empty] | 1.205 | 7.49
1.21 | 7.53 | 6.4 | [5 empty] | 1.21 | 7.53
1.215 | 7.56 | 6.43 | [5 empty] | 1.215 | 7.56
1.22 | 7.6 | 6.46 | [5 empty] | 1.22 | 7.6
1.225 | 7.63 | 6.48 | [5 empty] | 1.225 | 7.63
1.23 | 7.66 | 6.51 | [5 empty] | 1.23 | 7.66
1.235 | 7.7 | 6.54 | [5 empty] | 1.235 | 7.7
1.24 | 7.73 | 6.57 | [5 empty] | 1.24 | 7.73
1.245 | 7.76 | 6.6 | [5 empty] | 1.245 | 7.76
1.25 | 7.8 | 6.63 | [5 empty] | 1.25 | 7.8
1.255 | 7.83 | 6.66 | [5 empty] | 1.255 | 7.83
1.26 | 7.87 | 6.69 | [5 empty] | 1.26 | 7.87
1.265 | 7.9 | 6.71 | [5 empty] | 1.265 | 7.9
1.27 | 7.93 | 6.74 | [5 empty] | 1.27 | 7.93
1.275 | 7.97 | 6.77 | [5 empty] | 1.275 | 7.97
1.28 | 8 | 6.8 | [5 empty] | 1.28 | 8
1.285 | 8.03 | 6.83 | [5 empty] | 1.285 | 8.03
1.29 | 8.07 | 6.86 | [5 empty] | 1.29 | 8.07
1.295 | 8.1 | 6.89 | [5 empty] | 1.295 | 8.1
1.3 | 8.14 | 6.92 | -0.14 |  |  |  |  | 1.3 | 8.14
1.305 | 8.17 | 6.94 | [5 empty] | 1.305 | 8.17
1.31 | 8.2 | 6.97 | [5 empty] | 1.31 | 8.2
1.315 | 8.24 | 7 | [5 empty] | 1.315 | 8.24
1.32 | 8.27 | 7.03 | [5 empty] | 1.32 | 8.27
1.325 | 8.3 | 7.06 | [5 empty] | 1.325 | 8.3
1.33 | 8.34 | 7.09 | [5 empty] | 1.33 | 8.34
1.335 | 8.37 | 7.12 | [5 empty] | 1.335 | 8.37
1.34 | 8.41 | 7.14 | [5 empty] | 1.34 | 8.41
1.345 | 8.44 | 7.17 | [5 empty] | 1.345 | 8.44
1.35 | 8.47 | 7.2 | [5 empty] | 1.35 | 8.47
1.355 | 8.51 | 7.23 | [5 empty] | 1.355 | 8.51
1.36 | 8.54 | 7.26 | [5 empty] | 1.36 | 8.54
1.365 | 8.57 | 7.29 | [5 empty] | 1.365 | 8.57
1.37 | 8.61 | 7.32 | [5 empty] | 1.37 | 8.61
1.375 | 8.64 | 7.35 | [5 empty] | 1.375 | 8.64
1.38 | 8.68 | 7.37 | [5 empty] | 1.38 | 8.68
1.385 | 8.71 | 7.4 | [5 empty] | 1.385 | 8.71
1.39 | 8.74 | 7.43 | [5 empty] | 1.39 | 8.74
1.395 | 8.78 | 7.46 | [5 empty] | 1.395 | 8.78
1.4 | 8.81 | 7.49 | 0.19 |  |  |  |  | 1.4 | 8.81
1.405 | 8.84 | 7.52 | [5 empty] | 1.405 | 8.84
1.41 | 8.88 | 7.55 | [5 empty] | 1.41 | 8.88
1.415 | 8.91 | 7.58 | [5 empty] | 1.415 | 8.91
1.42 | 8.95 | 7.6 | [5 empty] | 1.42 | 8.95
1.425 | 8.98 | 7.63 | [5 empty] | 1.425 | 8.98
1.43 | 9.01 | 7.66 | [5 empty] | 1.43 | 9.01
1.435 | 9.05 | 7.69 | [5 empty] | 1.435 | 9.05
1.44 | 9.08 | 7.72 | [5 empty] | 1.44 | 9.08
1.445 | 9.11 | 7.75 | [5 empty] | 1.445 | 9.11
1.45 | 9.15 | 7.78 | [5 empty] | 1.45 | 9.15
1.455 | 9.18 | 7.8 | [5 empty] | 1.455 | 9.18
1.46 | 9.22 | 7.83 | [5 empty] | 1.46 | 9.22
1.465 | 9.25 | 7.86 | [5 empty] | 1.465 | 9.25
1.47 | 9.28 | 7.89 | [5 empty] | 1.47 | 9.28
1.475 | 9.32 | 7.92 | [5 empty] | 1.475 | 9.32
1.48 | 9.35 | 7.95 | [5 empty] | 1.48 | 9.35
1.485 | 9.38 | 7.98 | [5 empty] | 1.485 | 9.38
1.49 | 9.42 | 8.01 | [5 empty] | 1.49 | 9.42
1.495 | 9.45 | 8.03 | [5 empty] | 1.495 | 9.45
1.5 | 9.49 | 8.06 | 0.01 |  |  |  |  | 1.5 | 9.49
1.505 | 9.52 | 8.09 | [5 empty] | 1.505 | 9.52
1.51 | 9.55 | 8.12 | [5 empty] | 1.51 | 9.55
1.515 | 9.59 | 8.15 | [5 empty] | 1.515 | 9.59
1.52 | 9.62 | 8.18 | [5 empty] | 1.52 | 9.62
1.525 | 9.65 | 8.21 | [5 empty] | 1.525 | 9.65
1.53 | 9.69 | 8.23 | [5 empty] | 1.53 | 9.69
1.535 | 9.72 | 8.26 | [5 empty] | 1.535 | 9.72
1.54 | 9.76 | 8.29 | [5 empty] | 1.54 | 9.76
1.545 | 9.79 | 8.32 | [5 empty] | 1.545 | 9.79
1.55 | 9.82 | 8.35 | [5 empty] | 1.55 | 9.82
1.555 | 9.86 | 8.38 | [5 empty] | 1.555 | 9.86
1.56 | 9.89 | 8.41 | [5 empty] | 1.56 | 9.89
1.565 | 9.92 | 8.44 | [5 empty] | 1.565 | 9.92
1.57 | 9.96 | 8.46 | [5 empty] | 1.57 | 9.96
1.575 | 9.99 | 8.49 | [5 empty] | 1.575 | 9.99
1.58 | 10.03 | 8.52 | [5 empty] | 1.58 | 10.03
1.585 | 10.06 | 8.55 | [5 empty] | 1.585 | 10.06
1.59 | 10.09 | 8.58 | [5 empty] | 1.59 | 10.09
1.595 | 10.13 | 8.61 | [5 empty] | 1.595 | 10.13
1.6 | 10.16 | 8.64 | -0.16 |  |  |  |  | 1.6 | 10.16
1.605 | 10.19 | 8.67 | [5 empty] | 1.605 | 10.19
1.61 | 10.23 | 8.69 | [5 empty] | 1.61 | 10.23
1.615 | 10.26 | 8.72 | [5 empty] | 1.615 | 10.26
1.62 | 10.3 | 8.75 | [5 empty] | 1.62 | 10.3
1.625 | 10.33 | 8.78 | [5 empty] | 1.625 | 10.33
1.63 | 10.36 | 8.81 | [5 empty] | 1.63 | 10.36
1.635 | 10.4 | 8.84 | [5 empty] | 1.635 | 10.4
1.64 | 10.43 | 8.87 | [5 empty] | 1.64 | 10.43
1.645 | 10.46 | 8.89 | [5 empty] | 1.645 | 10.46
1.65 | 10.5 | 8.92 | [5 empty] | 1.65 | 10.5
1.655 | 10.53 | 8.95 | [5 empty] | 1.655 | 10.53
1.66 | 10.57 | 8.98 | [5 empty] | 1.66 | 10.57
1.665 | 10.6 | 9.01 | [5 empty] | 1.665 | 10.6
1.67 | 10.63 | 9.04 | [5 empty] | 1.67 | 10.63
1.675 | 10.67 | 9.07 | [5 empty] | 1.675 | 10.67
1.68 | 10.7 | 9.1 | [5 empty] | 1.68 | 10.7
1.685 | 10.73 | 9.12 | [5 empty] | 1.685 | 10.73
1.69 | 10.77 | 9.15 | [5 empty] | 1.69 | 10.77
1.695 | 10.8 | 9.18 | [5 empty] | 1.695 | 10.8
1.7 | 10.84 | 9.21 | 0.11 |  |  |  |  | 1.7 | 10.84
1.705 | 10.87 | 9.24 | [5 empty] | 1.705 | 10.87
1.71 | 10.9 | 9.27 | [5 empty] | 1.71 | 10.9
1.715 | 10.94 | 9.3 | [5 empty] | 1.715 | 10.94
1.72 | 10.97 | 9.33 | [5 empty] | 1.72 | 10.97
1.725 | 11 | 9.35 | [5 empty] | 1.725 | 11
1.73 | 11.04 | 9.38 | [5 empty] | 1.73 | 11.04
1.735 | 11.07 | 9.41 | [5 empty] | 1.735 | 11.07
1.74 | 11.11 | 9.44 | [5 empty] | 1.74 | 11.11
1.745 | 11.14 | 9.47 | [5 empty] | 1.745 | 11.14
1.75 | 11.17 | 9.5 | [5 empty] | 1.75 | 11.17
1.755 | 11.21 | 9.53 | [5 empty] | 1.755 | 11.21
1.76 | 11.24 | 9.55 | [5 empty] | 1.76 | 11.24
1.765 | 11.27 | 9.58 | [5 empty] | 1.765 | 11.27
1.77 | 11.31 | 9.61 | [5 empty] | 1.77 | 11.31
1.775 | 11.34 | 9.64 | [5 empty] | 1.775 | 11.34
1.78 | 11.38 | 9.67 | [5 empty] | 1.78 | 11.38
1.785 | 11.41 | 9.7 | [5 empty] | 1.785 | 11.41
1.79 | 11.44 | 9.73 | [5 empty] | 1.79 | 11.44
1.795 | 11.48 | 9.76 | [5 empty] | 1.795 | 11.48
1.8 | 11.51 | 9.78 | 0.29 |  |  |  |  | 1.8 | 11.51
1.805 | 11.54 | 9.81 | [5 empty] | 1.805 | 11.54
1.81 | 11.58 | 9.84 | [5 empty] | 1.81 | 11.58
1.815 | 11.61 | 9.87 | [5 empty] | 1.815 | 11.61
1.82 | 11.65 | 9.9 | [5 empty] | 1.82 | 11.65
1.825 | 11.68 | 9.93 | [5 empty] | 1.825 | 11.68
1.83 | 11.71 | 9.96 | [5 empty] | 1.83 | 11.71
1.835 | 11.75 | 9.98 | [5 empty] | 1.835 | 11.75
1.84 | 11.78 | 10.01 | [5 empty] | 1.84 | 11.78
1.845 | 11.81 | 10.04 | [5 empty] | 1.845 | 11.81
1.85 | 11.85 | 10.07 | [5 empty] | 1.85 | 11.85
1.855 | 11.88 | 10.1 | [5 empty] | 1.855 | 11.88
1.86 | 11.92 | 10.13 | [5 empty] | 1.86 | 11.92
1.865 | 11.95 | 10.16 | [5 empty] | 1.865 | 11.95
1.87 | 11.98 | 10.19 | [5 empty] | 1.87 | 11.98
1.875 | 12.02 | 10.21 | [5 empty] | 1.875 | 12.02
1.88 | 12.05 | 10.24 | [5 empty] | 1.88 | 12.05
1.885 | 12.08 | 10.27 | [5 empty] | 1.885 | 12.08
1.89 | 12.12 | 10.3 | [5 empty] | 1.89 | 12.12
1.895 | 12.15 | 10.33 | [5 empty] | 1.895 | 12.15
1.9 | 12.19 | 10.36 | -0.19 |  |  |  |  | 1.9 | 12.19
1.905 | 12.22 | 10.39 | [5 empty] | 1.905 | 12.22
1.91 | 12.25 | 10.42 | [5 empty] | 1.91 | 12.25
1.915 | 12.29 | 10.44 | [5 empty] | 1.915 | 12.29
1.92 | 12.32 | 10.47 | [5 empty] | 1.92 | 12.32
1.925 | 12.35 | 10.5 | [5 empty] | 1.925 | 12.35
1.93 | 12.39 | 10.53 | [5 empty] | 1.93 | 12.39
1.935 | 12.42 | 10.56 | [5 empty] | 1.935 | 12.42
1.94 | 12.46 | 10.59 | [5 empty] | 1.94 | 12.46
1.945 | 12.49 | 10.62 | [5 empty] | 1.945 | 12.49
1.95 | 12.52 | 10.64 | [5 empty] | 1.95 | 12.52
1.955 | 12.56 | 10.67 | [5 empty] | 1.955 | 12.56
1.96 | 12.59 | 10.7 | [5 empty] | 1.96 | 12.59
1.965 | 12.62 | 10.73 | [5 empty] | 1.965 | 12.62
1.97 | 12.66 | 10.76 | [5 empty] | 1.97 | 12.66
1.975 | 12.69 | 10.79 | [5 empty] | 1.975 | 12.69
1.98 | 12.73 | 10.82 | [5 empty] | 1.98 | 12.73
1.985 | 12.76 | 10.85 | [5 empty] | 1.985 | 12.76
1.99 | 12.79 | 10.87 | [5 empty] | 1.99 | 12.79
1.995 | 12.83 | 10.9 | [5 empty] | 1.995 | 12.83
2 | 12.86 | 10.93 | -0.36 |  |  |  |  | 2 | 12.86
2.005 | 12.89 | 10.96 | [5 empty] | 2.005 | 12.89
2.01 | 12.93 | 10.99 | [5 empty] | 2.01 | 12.93
2.015 | 12.96 | 11.02 | [5 empty] | 2.015 | 12.96
2.02 | 13 | 11.05 | [5 empty] | 2.02 | 13
2.025 | 13.03 | 11.07 | [5 empty] | 2.025 | 13.03
2.03 | 13.06 | 11.1 | [5 empty] | 2.03 | 13.06
2.03 | 13.06 | 11.1 | -0.06 |  |  |  |  | 2.03 | 13.06

## Sounding Table_Calibrated
SoundingTable Base |  |  |  |  | Sounding Table - Calibration Points |  |  | Calibration Points - Linearisation
Level_m | Volume_m3 | Weight | Correction_factor | Revised Value = Volume_m3 + Correction_factor | Level_m | Corrected_Volume_m3 | Entered_Correction_factor | Level_m | InterPoluted_Volume_m3 |  | Level_m | Volume_m3 | Volume_m3 | Correction_factor
0 | 0.03 | 0.02 | 0.01 | 0.04 | 0 | 0.04 | 0.01 | 0 | 0.04 | Note: Calculation was done for first two correction factors | 0 | 0.03 | 0.04 | 0.01
0.005 | 0.03 | 0.03 | 0.0195 | 0.0495 | 0.1 | 0.23 | -0.03 | 0.005 | 0.0495 |  | 0.1 | 0.26 | 0.23 | -0.03
0.01 | 0.04 | 0.03 | 0.019 | 0.059 | 0.2 | 0.85 | 0.12 | 0.01 | 0.059 |  | 0.2 | 0.73 | 0.85 | 0.12
0.015 | 0.05 | 0.04 | 0.0185 | 0.0685 | 0.3 | 1.15 | -0.24 | 0.015 | 0.0685 |  | 0.3 | 1.39 | 1.15 | -0.24
0.02 | 0.05 | 0.05 | 0.028 | 0.078 | 0.4 | 2 | -0.06 | 0.02 | 0.078 |  | 0.4 | 2.06 | 2 | -0.06
0.025 | 0.06 | 0.05 | 0.0275 | 0.0875 | 0.5 | 2.5 | -0.24 | 0.025 | 0.0875 | Steps: | 0.5 | 2.74 | 2.5 | -0.24
0.03 | 0.07 | 0.06 | 0.027 | 0.097 | 0.6 | 3.23 | -0.18 | 0.03 | 0.097 | 1. Look up the correction factor’s volume and add it . | 0.6 | 3.41 | 3.23 | -0.18
0.035 | 0.08 | 0.07 | 0.0265 | 0.1065 | 0.7 | 4.25 | 0.16 | 0.035 | 0.1065 | 2.Perform linear calculation using the corrected volume and level, applying upto the next correction factor. | 0.7 | 4.09 | 4.25 | 0.16
0.04 | 0.09 | 0.08 | 0.026 | 0.116 | 0.8 | 4.9 | 0.14 | 0.04 | 0.116 |  | 0.8 | 4.76 | 4.9 | 0.14
0.045 | 0.1 | 0.09 | 0.0255 | 0.1255 | 0.9 | 5.25 | -0.19 | 0.045 | 0.1255 | Formula: | 0.9 | 5.44 | 5.25 | -0.19
0.05 | 0.11 | 0.1 | 0.025 | 0.135 | 1 | 6 | -0.11 | 0.05 | 0.135 | V=V1+((L−L1)/(L2−L1))*(V2−V1) | 1 | 6.11 | 6 | -0.11
0.055 | 0.12 | 0.11 | 0.0245 | 0.1445 | 1.1 | 6.5 | -0.29 | 0.055 | 0.1445 | Linear Interpolution=CorrectedV1 + ((Level - Level1) / (Level2 - Level1)) * (CorrectedV2 - CorrectedV1) | 1.1 | 6.79 | 6.5 | -0.29
0.06 | 0.14 | 0.12 | 0.014 | 0.154 | 1.2 | 7.35 | -0.11 | 0.06 | 0.154 |  | 1.2 | 7.46 | 7.35 | -0.11
0.065 | 0.15 | 0.13 | 0.0135 | 0.1635 | 1.3 | 8 | -0.14 | 0.065 | 0.1635 | CorrectedV1- Calibrated first volume range(I-coloumn) | 1.3 | 8.14 | 8 | -0.14
0.07 | 0.16 | 0.14 | 0.013 | 0.173 | 1.4 | 9 | 0.19 | 0.07 | 0.173 | CorrectedV2- Calibrated next volume range(I-coloumn) | 1.4 | 8.81 | 9 | 0.19
0.075 | 0.18 | 0.15 | 0.0025 | 0.1825 | 1.5 | 9.5 | 0.01 | 0.075 | 0.1825 | Level-current level(L-coloumn) | 1.5 | 9.49 | 9.5 | 0.01
0.08 | 0.19 | 0.16 | 0.002 | 0.192 | 1.6 | 10 | -0.16 | 0.08 | 0.192 | Level1-frist range in H coloumn | 1.6 | 10.16 | 10 | -0.16
0.085 | 0.21 | 0.18 | -0.0085 | 0.2015 | 1.7 | 10.95 | 0.11 | 0.085 | 0.2015 | Level2-Next range in H coloumn | 1.7 | 10.84 | 10.95 | 0.11
0.09 | 0.22 | 0.19 | -0.009 | 0.211 | 1.8 | 11.8 | 0.29 | 0.09 | 0.211 |  | 1.8 | 11.51 | 11.8 | 0.29
0.095 | 0.24 | 0.2 | -0.0195 | 0.2205 | 1.9 | 12 | -0.19 | 0.095 | 0.2205 |  | 1.9 | 12.19 | 12 | -0.19
0.1 | 0.26 | 0.22 | -0.03 | 0.23 | 2 | 12.5 | -0.36 | 0.1 | 0.23 |  | 2 | 12.86 | 12.5 | -0.36
0.105 | 0.28 | 0.23 |  |  | 2.03 | 13 | -0.06 | 0.105 |  | Legends: | 2.03 | 13.06 | 13 | -0.06
0.11 | 0.29 | 0.25 | [5 empty] | 0.11 |  | Entered_Correction_factors
0.115 | 0.31 | 0.27 | [5 empty] | 0.115 |  | Calculated Interpolution values
0.12 | 0.33 | 0.28 | [5 empty] | 0.12 |  | used for Linear Interpolution calculation
0.125 | 0.35 | 0.3 | [5 empty] | 0.125 |  | Calculated Correction_factors
0.13 | 0.37 | 0.32 | [5 empty] | 0.13
0.135 | 0.4 | 0.34 | [5 empty] | 0.135
0.14 | 0.42 | 0.35 | [5 empty] | 0.14
0.145 | 0.44 | 0.37 | [5 empty] | 0.145
0.15 | 0.46 | 0.39 | [5 empty] | 0.15
0.155 | 0.49 | 0.41 | [5 empty] | 0.155
0.16 | 0.51 | 0.43 | [5 empty] | 0.16
0.165 | 0.54 | 0.46 | [5 empty] | 0.165
0.17 | 0.56 | 0.48 | [5 empty] | 0.17
0.175 | 0.59 | 0.5 | [5 empty] | 0.175
0.18 | 0.61 | 0.52 | [5 empty] | 0.18
0.185 | 0.64 | 0.55 | [5 empty] | 0.185
0.19 | 0.67 | 0.57 | [5 empty] | 0.19
0.195 | 0.7 | 0.59 | [5 empty] | 0.195
0.2 | 0.73 | 0.62 | 0.12 |  |  |  |  | 0.2
0.205 | 0.76 | 0.64 | [5 empty] | 0.205
0.21 | 0.79 | 0.67 | [5 empty] | 0.21
0.215 | 0.82 | 0.7 | [5 empty] | 0.215
0.22 | 0.85 | 0.72 | [5 empty] | 0.22
0.225 | 0.88 | 0.75 | [5 empty] | 0.225
0.23 | 0.92 | 0.78 | [5 empty] | 0.23
0.235 | 0.95 | 0.81 | [5 empty] | 0.235
0.24 | 0.98 | 0.83 | [5 empty] | 0.24
0.245 | 1.01 | 0.86 | [5 empty] | 0.245
0.25 | 1.05 | 0.89 | [5 empty] | 0.25
0.255 | 1.08 | 0.92 | [5 empty] | 0.255
0.26 | 1.12 | 0.95 | [5 empty] | 0.26
0.265 | 1.15 | 0.98 | [5 empty] | 0.265
0.27 | 1.18 | 1.01 | [5 empty] | 0.27
0.275 | 1.22 | 1.03 | [5 empty] | 0.275
0.28 | 1.25 | 1.06 | [5 empty] | 0.28
0.285 | 1.28 | 1.09 | [5 empty] | 0.285
0.29 | 1.32 | 1.12 | [5 empty] | 0.29
0.295 | 1.35 | 1.15 | [5 empty] | 0.295
0.3 | 1.39 | 1.18 | -0.24 |  |  |  |  | 0.3
0.305 | 1.42 | 1.21 | [5 empty] | 0.305
0.31 | 1.45 | 1.24 | [5 empty] | 0.31
0.315 | 1.49 | 1.26 | [5 empty] | 0.315
0.32 | 1.52 | 1.29 | [5 empty] | 0.32
0.325 | 1.55 | 1.32 | [5 empty] | 0.325
0.33 | 1.59 | 1.35 | [5 empty] | 0.33
0.335 | 1.62 | 1.38 | [5 empty] | 0.335
0.34 | 1.66 | 1.41 | [5 empty] | 0.34
0.345 | 1.69 | 1.44 | [5 empty] | 0.345
0.35 | 1.72 | 1.46 | [5 empty] | 0.35
0.355 | 1.76 | 1.49 | [5 empty] | 0.355
0.36 | 1.79 | 1.52 | [5 empty] | 0.36
0.365 | 1.82 | 1.55 | [5 empty] | 0.365
0.37 | 1.86 | 1.58 | [5 empty] | 0.37
0.375 | 1.89 | 1.61 | [5 empty] | 0.375
0.38 | 1.93 | 1.64 | [5 empty] | 0.38
0.385 | 1.96 | 1.67 | [5 empty] | 0.385
0.39 | 1.99 | 1.69 | [5 empty] | 0.39
0.395 | 2.03 | 1.72 | [5 empty] | 0.395
0.4 | 2.06 | 1.75 | -0.06 |  |  |  |  | 0.4
0.405 | 2.09 | 1.78 | [5 empty] | 0.405
0.41 | 2.13 | 1.81 | [5 empty] | 0.41
0.415 | 2.16 | 1.84 | [5 empty] | 0.415
0.42 | 2.2 | 1.87 | [5 empty] | 0.42
0.425 | 2.23 | 1.89 | [5 empty] | 0.425
0.43 | 2.26 | 1.92 | [5 empty] | 0.43
0.435 | 2.3 | 1.95 | [5 empty] | 0.435
0.44 | 2.33 | 1.98 | [5 empty] | 0.44
0.445 | 2.36 | 2.01 | [5 empty] | 0.445
0.45 | 2.4 | 2.04 | [5 empty] | 0.45
0.455 | 2.43 | 2.07 | [5 empty] | 0.455
0.46 | 2.47 | 2.1 | [5 empty] | 0.46
0.465 | 2.5 | 2.12 | [5 empty] | 0.465
0.47 | 2.53 | 2.15 | [5 empty] | 0.47
0.475 | 2.57 | 2.18 | [5 empty] | 0.475
0.48 | 2.6 | 2.21 | [5 empty] | 0.48
0.485 | 2.63 | 2.24 | [5 empty] | 0.485
0.49 | 2.67 | 2.27 | [5 empty] | 0.49
0.495 | 2.7 | 2.3 | [5 empty] | 0.495
0.5 | 2.74 | 2.33 | -0.24 |  |  |  |  | 0.5
0.505 | 2.77 | 2.35 | [5 empty] | 0.505
0.51 | 2.8 | 2.38 | [5 empty] | 0.51
0.515 | 2.84 | 2.41 | [5 empty] | 0.515
0.52 | 2.87 | 2.44 | [5 empty] | 0.52
0.525 | 2.9 | 2.47 | [5 empty] | 0.525
0.53 | 2.94 | 2.5 | [5 empty] | 0.53
0.535 | 2.97 | 2.53 | [5 empty] | 0.535
0.54 | 3.01 | 2.55 | [5 empty] | 0.54
0.545 | 3.04 | 2.58 | [5 empty] | 0.545
0.55 | 3.07 | 2.61 | [5 empty] | 0.55
0.555 | 3.11 | 2.64 | [5 empty] | 0.555
0.56 | 3.14 | 2.67 | [5 empty] | 0.56
0.565 | 3.17 | 2.7 | [5 empty] | 0.565
0.57 | 3.21 | 2.73 | [5 empty] | 0.57
0.575 | 3.24 | 2.76 | [5 empty] | 0.575
0.58 | 3.28 | 2.78 | [5 empty] | 0.58
0.585 | 3.31 | 2.81 | [5 empty] | 0.585
0.59 | 3.34 | 2.84 | [5 empty] | 0.59
0.595 | 3.38 | 2.87 | [5 empty] | 0.595
0.6 | 3.41 | 2.9 | -0.18 |  |  |  |  | 0.6
0.605 | 3.44 | 2.93 | [5 empty] | 0.605
0.61 | 3.48 | 2.96 | [5 empty] | 0.61
0.615 | 3.51 | 2.99 | [5 empty] | 0.615
0.62 | 3.55 | 3.01 | [5 empty] | 0.62
0.625 | 3.58 | 3.04 | [5 empty] | 0.625
0.63 | 3.61 | 3.07 | [5 empty] | 0.63
0.635 | 3.65 | 3.1 | [5 empty] | 0.635
0.64 | 3.68 | 3.13 | [5 empty] | 0.64
0.645 | 3.71 | 3.16 | [5 empty] | 0.645
0.65 | 3.75 | 3.19 | [5 empty] | 0.65
0.655 | 3.78 | 3.21 | [5 empty] | 0.655
0.66 | 3.82 | 3.24 | [5 empty] | 0.66
0.665 | 3.85 | 3.27 | [5 empty] | 0.665
0.67 | 3.88 | 3.3 | [5 empty] | 0.67
0.675 | 3.92 | 3.33 | [5 empty] | 0.675
0.68 | 3.95 | 3.36 | [5 empty] | 0.68
0.685 | 3.98 | 3.39 | [5 empty] | 0.685
0.69 | 4.02 | 3.42 | [5 empty] | 0.69
0.695 | 4.05 | 3.44 | [5 empty] | 0.695
0.7 | 4.09 | 3.47 | 0.16 |  |  |  |  | 0.7
0.705 | 4.12 | 3.5 | [5 empty] | 0.705
0.71 | 4.15 | 3.53 | [5 empty] | 0.71
0.715 | 4.19 | 3.56 | [5 empty] | 0.715
0.72 | 4.22 | 3.59 | [5 empty] | 0.72
0.725 | 4.25 | 3.62 | [5 empty] | 0.725
0.73 | 4.29 | 3.64 | [5 empty] | 0.73
0.735 | 4.32 | 3.67 | [5 empty] | 0.735
0.74 | 4.36 | 3.7 | [5 empty] | 0.74
0.745 | 4.39 | 3.73 | [5 empty] | 0.745
0.75 | 4.42 | 3.76 | [5 empty] | 0.75
0.755 | 4.46 | 3.79 | [5 empty] | 0.755
0.76 | 4.49 | 3.82 | [5 empty] | 0.76
0.765 | 4.52 | 3.85 | [5 empty] | 0.765
0.77 | 4.56 | 3.87 | [5 empty] | 0.77
0.775 | 4.59 | 3.9 | [5 empty] | 0.775
0.78 | 4.63 | 3.93 | [5 empty] | 0.78
0.785 | 4.66 | 3.96 | [5 empty] | 0.785
0.79 | 4.69 | 3.99 | [5 empty] | 0.79
0.795 | 4.73 | 4.02 | [5 empty] | 0.795
0.8 | 4.76 | 4.05 | 0.14 |  |  |  |  | 0.8
0.805 | 4.79 | 4.08 | [5 empty] | 0.805
0.81 | 4.83 | 4.1 | [5 empty] | 0.81
0.815 | 4.86 | 4.13 | [5 empty] | 0.815
0.82 | 4.9 | 4.16 | [5 empty] | 0.82
0.825 | 4.93 | 4.19 | [5 empty] | 0.825
0.83 | 4.96 | 4.22 | [5 empty] | 0.83
0.835 | 5 | 4.25 | [5 empty] | 0.835
0.84 | 5.03 | 4.28 | [5 empty] | 0.84
0.845 | 5.06 | 4.3 | [5 empty] | 0.845
0.85 | 5.1 | 4.33 | [5 empty] | 0.85
0.855 | 5.13 | 4.36 | [5 empty] | 0.855
0.86 | 5.17 | 4.39 | [5 empty] | 0.86
0.865 | 5.2 | 4.42 | [5 empty] | 0.865
0.87 | 5.23 | 4.45 | [5 empty] | 0.87
0.875 | 5.27 | 4.48 | [5 empty] | 0.875
0.88 | 5.3 | 4.51 | [5 empty] | 0.88
0.885 | 5.33 | 4.53 | [5 empty] | 0.885
0.89 | 5.37 | 4.56 | [5 empty] | 0.89
0.895 | 5.4 | 4.59 | [5 empty] | 0.895
0.9 | 5.44 | 4.62 | -0.19 |  |  |  |  | 0.9
0.905 | 5.47 | 4.65 | [5 empty] | 0.905
0.91 | 5.5 | 4.68 | [5 empty] | 0.91
0.915 | 5.54 | 4.71 | [5 empty] | 0.915
0.92 | 5.57 | 4.74 | [5 empty] | 0.92
0.925 | 5.6 | 4.76 | [5 empty] | 0.925
0.93 | 5.64 | 4.79 | [5 empty] | 0.93
0.935 | 5.67 | 4.82 | [5 empty] | 0.935
0.94 | 5.71 | 4.85 | [5 empty] | 0.94
0.945 | 5.74 | 4.88 | [5 empty] | 0.945
0.95 | 5.77 | 4.91 | [5 empty] | 0.95
0.955 | 5.81 | 4.94 | [5 empty] | 0.955
0.96 | 5.84 | 4.96 | [5 empty] | 0.96
0.965 | 5.87 | 4.99 | [5 empty] | 0.965
0.97 | 5.91 | 5.02 | [5 empty] | 0.97
0.975 | 5.94 | 5.05 | [5 empty] | 0.975
0.98 | 5.98 | 5.08 | [5 empty] | 0.98
0.985 | 6.01 | 5.11 | [5 empty] | 0.985
0.99 | 6.04 | 5.14 | [5 empty] | 0.99
0.995 | 6.08 | 5.17 | [5 empty] | 0.995
1 | 6.11 | 5.19 | -0.11 |  |  |  |  | 1
1.005 | 6.14 | 5.22 | [5 empty] | 1.005
1.01 | 6.18 | 5.25 | [5 empty] | 1.01
1.015 | 6.21 | 5.28 | [5 empty] | 1.015
1.02 | 6.25 | 5.31 | [5 empty] | 1.02
1.025 | 6.28 | 5.34 | [5 empty] | 1.025
1.03 | 6.31 | 5.37 | [5 empty] | 1.03
1.035 | 6.35 | 5.39 | [5 empty] | 1.035
1.04 | 6.38 | 5.42 | [5 empty] | 1.04
1.045 | 6.41 | 5.45 | [5 empty] | 1.045
1.05 | 6.45 | 5.48 | [5 empty] | 1.05
1.055 | 6.48 | 5.51 | [5 empty] | 1.055
1.06 | 6.52 | 5.54 | [5 empty] | 1.06
1.065 | 6.55 | 5.57 | [5 empty] | 1.065
1.07 | 6.58 | 5.6 | [5 empty] | 1.07
1.075 | 6.62 | 5.62 | [5 empty] | 1.075
1.08 | 6.65 | 5.65 | [5 empty] | 1.08
1.085 | 6.68 | 5.68 | [5 empty] | 1.085
1.09 | 6.72 | 5.71 | [5 empty] | 1.09
1.095 | 6.75 | 5.74 | [5 empty] | 1.095
1.1 | 6.79 | 5.77 | -0.29 |  |  |  |  | 1.1
1.105 | 6.82 | 5.8 | [5 empty] | 1.105
1.11 | 6.85 | 5.83 | [5 empty] | 1.11
1.115 | 6.89 | 5.85 | [5 empty] | 1.115
1.12 | 6.92 | 5.88 | [5 empty] | 1.12
1.125 | 6.95 | 5.91 | [5 empty] | 1.125
1.13 | 6.99 | 5.94 | [5 empty] | 1.13
1.135 | 7.02 | 5.97 | [5 empty] | 1.135
1.14 | 7.06 | 6 | [5 empty] | 1.14
1.145 | 7.09 | 6.03 | [5 empty] | 1.145
1.15 | 7.12 | 6.05 | [5 empty] | 1.15
1.155 | 7.16 | 6.08 | [5 empty] | 1.155
1.16 | 7.19 | 6.11 | [5 empty] | 1.16
1.165 | 7.22 | 6.14 | [5 empty] | 1.165
1.17 | 7.26 | 6.17 | [5 empty] | 1.17
1.175 | 7.29 | 6.2 | [5 empty] | 1.175
1.18 | 7.33 | 6.23 | [5 empty] | 1.18
1.185 | 7.36 | 6.26 | [5 empty] | 1.185
1.19 | 7.39 | 6.28 | [5 empty] | 1.19
1.195 | 7.43 | 6.31 | [5 empty] | 1.195
1.2 | 7.46 | 6.34 | -0.11 |  |  |  |  | 1.2
1.205 | 7.49 | 6.37 | [5 empty] | 1.205
1.21 | 7.53 | 6.4 | [5 empty] | 1.21
1.215 | 7.56 | 6.43 | [5 empty] | 1.215
1.22 | 7.6 | 6.46 | [5 empty] | 1.22
1.225 | 7.63 | 6.48 | [5 empty] | 1.225
1.23 | 7.66 | 6.51 | [5 empty] | 1.23
1.235 | 7.7 | 6.54 | [5 empty] | 1.235
1.24 | 7.73 | 6.57 | [5 empty] | 1.24
1.245 | 7.76 | 6.6 | [5 empty] | 1.245
1.25 | 7.8 | 6.63 | [5 empty] | 1.25
1.255 | 7.83 | 6.66 | [5 empty] | 1.255
1.26 | 7.87 | 6.69 | [5 empty] | 1.26
1.265 | 7.9 | 6.71 | [5 empty] | 1.265
1.27 | 7.93 | 6.74 | [5 empty] | 1.27
1.275 | 7.97 | 6.77 | [5 empty] | 1.275
1.28 | 8 | 6.8 | [5 empty] | 1.28
1.285 | 8.03 | 6.83 | [5 empty] | 1.285
1.29 | 8.07 | 6.86 | [5 empty] | 1.29
1.295 | 8.1 | 6.89 | [5 empty] | 1.295
1.3 | 8.14 | 6.92 | -0.14 |  |  |  |  | 1.3
1.305 | 8.17 | 6.94 | [5 empty] | 1.305
1.31 | 8.2 | 6.97 | [5 empty] | 1.31
1.315 | 8.24 | 7 | [5 empty] | 1.315
1.32 | 8.27 | 7.03 | [5 empty] | 1.32
1.325 | 8.3 | 7.06 | [5 empty] | 1.325
1.33 | 8.34 | 7.09 | [5 empty] | 1.33
1.335 | 8.37 | 7.12 | [5 empty] | 1.335
1.34 | 8.41 | 7.14 | [5 empty] | 1.34
1.345 | 8.44 | 7.17 | [5 empty] | 1.345
1.35 | 8.47 | 7.2 | [5 empty] | 1.35
1.355 | 8.51 | 7.23 | [5 empty] | 1.355
1.36 | 8.54 | 7.26 | [5 empty] | 1.36
1.365 | 8.57 | 7.29 | [5 empty] | 1.365
1.37 | 8.61 | 7.32 | [5 empty] | 1.37
1.375 | 8.64 | 7.35 | [5 empty] | 1.375
1.38 | 8.68 | 7.37 | [5 empty] | 1.38
1.385 | 8.71 | 7.4 | [5 empty] | 1.385
1.39 | 8.74 | 7.43 | [5 empty] | 1.39
1.395 | 8.78 | 7.46 | [5 empty] | 1.395
1.4 | 8.81 | 7.49 | 0.19 |  |  |  |  | 1.4
1.405 | 8.84 | 7.52 | [5 empty] | 1.405
1.41 | 8.88 | 7.55 | [5 empty] | 1.41
1.415 | 8.91 | 7.58 | [5 empty] | 1.415
1.42 | 8.95 | 7.6 | [5 empty] | 1.42
1.425 | 8.98 | 7.63 | [5 empty] | 1.425
1.43 | 9.01 | 7.66 | [5 empty] | 1.43
1.435 | 9.05 | 7.69 | [5 empty] | 1.435
1.44 | 9.08 | 7.72 | [5 empty] | 1.44
1.445 | 9.11 | 7.75 | [5 empty] | 1.445
1.45 | 9.15 | 7.78 | [5 empty] | 1.45
1.455 | 9.18 | 7.8 | [5 empty] | 1.455
1.46 | 9.22 | 7.83 | [5 empty] | 1.46
1.465 | 9.25 | 7.86 | [5 empty] | 1.465
1.47 | 9.28 | 7.89 | [5 empty] | 1.47
1.475 | 9.32 | 7.92 | [5 empty] | 1.475
1.48 | 9.35 | 7.95 | [5 empty] | 1.48
1.485 | 9.38 | 7.98 | [5 empty] | 1.485
1.49 | 9.42 | 8.01 | [5 empty] | 1.49
1.495 | 9.45 | 8.03 | [5 empty] | 1.495
1.5 | 9.49 | 8.06 | 0.01 |  |  |  |  | 1.5
1.505 | 9.52 | 8.09 | [5 empty] | 1.505
1.51 | 9.55 | 8.12 | [5 empty] | 1.51
1.515 | 9.59 | 8.15 | [5 empty] | 1.515
1.52 | 9.62 | 8.18 | [5 empty] | 1.52
1.525 | 9.65 | 8.21 | [5 empty] | 1.525
1.53 | 9.69 | 8.23 | [5 empty] | 1.53
1.535 | 9.72 | 8.26 | [5 empty] | 1.535
1.54 | 9.76 | 8.29 | [5 empty] | 1.54
1.545 | 9.79 | 8.32 | [5 empty] | 1.545
1.55 | 9.82 | 8.35 | [5 empty] | 1.55
1.555 | 9.86 | 8.38 | [5 empty] | 1.555
1.56 | 9.89 | 8.41 | [5 empty] | 1.56
1.565 | 9.92 | 8.44 | [5 empty] | 1.565
1.57 | 9.96 | 8.46 | [5 empty] | 1.57
1.575 | 9.99 | 8.49 | [5 empty] | 1.575
1.58 | 10.03 | 8.52 | [5 empty] | 1.58
1.585 | 10.06 | 8.55 | [5 empty] | 1.585
1.59 | 10.09 | 8.58 | [5 empty] | 1.59
1.595 | 10.13 | 8.61 | [5 empty] | 1.595
1.6 | 10.16 | 8.64 | -0.16 |  |  |  |  | 1.6
1.605 | 10.19 | 8.67 | [5 empty] | 1.605
1.61 | 10.23 | 8.69 | [5 empty] | 1.61
1.615 | 10.26 | 8.72 | [5 empty] | 1.615
1.62 | 10.3 | 8.75 | [5 empty] | 1.62
1.625 | 10.33 | 8.78 | [5 empty] | 1.625
1.63 | 10.36 | 8.81 | [5 empty] | 1.63
1.635 | 10.4 | 8.84 | [5 empty] | 1.635
1.64 | 10.43 | 8.87 | [5 empty] | 1.64
1.645 | 10.46 | 8.89 | [5 empty] | 1.645
1.65 | 10.5 | 8.92 | [5 empty] | 1.65
1.655 | 10.53 | 8.95 | [5 empty] | 1.655
1.66 | 10.57 | 8.98 | [5 empty] | 1.66
1.665 | 10.6 | 9.01 | [5 empty] | 1.665
1.67 | 10.63 | 9.04 | [5 empty] | 1.67
1.675 | 10.67 | 9.07 | [5 empty] | 1.675
1.68 | 10.7 | 9.1 | [5 empty] | 1.68
1.685 | 10.73 | 9.12 | [5 empty] | 1.685
1.69 | 10.77 | 9.15 | [5 empty] | 1.69
1.695 | 10.8 | 9.18 | [5 empty] | 1.695
1.7 | 10.84 | 9.21 | 0.11 |  |  |  |  | 1.7
1.705 | 10.87 | 9.24 | [5 empty] | 1.705
1.71 | 10.9 | 9.27 | [5 empty] | 1.71
1.715 | 10.94 | 9.3 | [5 empty] | 1.715
1.72 | 10.97 | 9.33 | [5 empty] | 1.72
1.725 | 11 | 9.35 | [5 empty] | 1.725
1.73 | 11.04 | 9.38 | [5 empty] | 1.73
1.735 | 11.07 | 9.41 | [5 empty] | 1.735
1.74 | 11.11 | 9.44 | [5 empty] | 1.74
1.745 | 11.14 | 9.47 | [5 empty] | 1.745
1.75 | 11.17 | 9.5 | [5 empty] | 1.75
1.755 | 11.21 | 9.53 | [5 empty] | 1.755
1.76 | 11.24 | 9.55 | [5 empty] | 1.76
1.765 | 11.27 | 9.58 | [5 empty] | 1.765
1.77 | 11.31 | 9.61 | [5 empty] | 1.77
1.775 | 11.34 | 9.64 | [5 empty] | 1.775
1.78 | 11.38 | 9.67 | [5 empty] | 1.78
1.785 | 11.41 | 9.7 | [5 empty] | 1.785
1.79 | 11.44 | 9.73 | [5 empty] | 1.79
1.795 | 11.48 | 9.76 | [5 empty] | 1.795
1.8 | 11.51 | 9.78 | 0.29 |  |  |  |  | 1.8
1.805 | 11.54 | 9.81 | [5 empty] | 1.805
1.81 | 11.58 | 9.84 | [5 empty] | 1.81
1.815 | 11.61 | 9.87 | [5 empty] | 1.815
1.82 | 11.65 | 9.9 | [5 empty] | 1.82
1.825 | 11.68 | 9.93 | [5 empty] | 1.825
1.83 | 11.71 | 9.96 | [5 empty] | 1.83
1.835 | 11.75 | 9.98 | [5 empty] | 1.835
1.84 | 11.78 | 10.01 | [5 empty] | 1.84
1.845 | 11.81 | 10.04 | [5 empty] | 1.845
1.85 | 11.85 | 10.07 | [5 empty] | 1.85
1.855 | 11.88 | 10.1 | [5 empty] | 1.855
1.86 | 11.92 | 10.13 | [5 empty] | 1.86
1.865 | 11.95 | 10.16 | [5 empty] | 1.865
1.87 | 11.98 | 10.19 | [5 empty] | 1.87
1.875 | 12.02 | 10.21 | [5 empty] | 1.875
1.88 | 12.05 | 10.24 | [5 empty] | 1.88
1.885 | 12.08 | 10.27 | [5 empty] | 1.885
1.89 | 12.12 | 10.3 | [5 empty] | 1.89
1.895 | 12.15 | 10.33 | [5 empty] | 1.895
1.9 | 12.19 | 10.36 | -0.19 |  |  |  |  | 1.9
1.905 | 12.22 | 10.39 | [5 empty] | 1.905
1.91 | 12.25 | 10.42 | [5 empty] | 1.91
1.915 | 12.29 | 10.44 | [5 empty] | 1.915
1.92 | 12.32 | 10.47 | [5 empty] | 1.92
1.925 | 12.35 | 10.5 | [5 empty] | 1.925
1.93 | 12.39 | 10.53 | [5 empty] | 1.93
1.935 | 12.42 | 10.56 | [5 empty] | 1.935
1.94 | 12.46 | 10.59 | [5 empty] | 1.94
1.945 | 12.49 | 10.62 | [5 empty] | 1.945
1.95 | 12.52 | 10.64 | [5 empty] | 1.95
1.955 | 12.56 | 10.67 | [5 empty] | 1.955
1.96 | 12.59 | 10.7 | [5 empty] | 1.96
1.965 | 12.62 | 10.73 | [5 empty] | 1.965
1.97 | 12.66 | 10.76 | [5 empty] | 1.97
1.975 | 12.69 | 10.79 | [5 empty] | 1.975
1.98 | 12.73 | 10.82 | [5 empty] | 1.98
1.985 | 12.76 | 10.85 | [5 empty] | 1.985
1.99 | 12.79 | 10.87 | [5 empty] | 1.99
1.995 | 12.83 | 10.9 | [5 empty] | 1.995
2 | 12.86 | 10.93 | -0.36 |  |  |  |  | 2
2.005 | 12.89 | 10.96 | [5 empty] | 2.005
2.01 | 12.93 | 10.99 | [5 empty] | 2.01
2.015 | 12.96 | 11.02 | [5 empty] | 2.015
2.02 | 13 | 11.05 | [5 empty] | 2.02
2.025 | 13.03 | 11.07 | [5 empty] | 2.025
2.03 | 13.06 | 11.1 | [5 empty] | 2.03
2.03 | 13.06 | 11.1 | -0.06 |  |  |  |  | 2.03